## 1;Test SVI FF New features
23 | Alarms testing - Case WRITE_LOCK - Advanced options |  |  |  | 15:0 | Windows 10 | Mihail Milev
|  | 1 | Get "RB.0.BLOCK_TAG" | Write down the received block tag.
|  | 2 | Get "RB.SOFTWARE_REV" | Write down the received version of the software,
|  | 3 | Use "Smart Assistant" and select "FF Device Content.Write Advanced.Advanced type" | "Advanced type" is selected
|  | 4 | Set "TB.DEVIATION_ALERT(26).ENABLE" to "1" | "TB.DEVIATION_ALERT(26).ENABLE" is set to "1"
|  | 5 | Set "TB.POSITION_HI-HI_ALERT(27).ENABLE" to "1" | "TB.POSITION_HI-HI_ALERT(27).ENABLE" is set to "1"
|  | 6 | Set "TB.POSITION_HI_ALERT(28).ENABLE" to "1" | "TB.POSITION_HI_ALERT(28).ENABLE" is set to "1"
|  | 7 | Set "TB.POSITION_LO_ALERT(29).ENABLE" to "1" | "TB.POSITION_LO_ALERT(29).ENABLE" is set to "1"
|  | 8 | Set "TB.POSITION_LOLO_ALERT(30).ENABLE" to "1" | "TB.POSITION_LOLO_ALERT(30).ENABLE" is set to "1"
|  | 9 | Set "TB.TRAVEL_ACCUMULATION_A_ALERT(31).ENABLE" to "1" | "TB.TRAVEL_ACCUMULATION_A_ALERT(31).ENABLEE" is set to "1"
|  | 10 | Set "TB.TRAVEL_ACCUMULATION_B_ALERT(32).ENABLE" to "1" | "TB.TRAVEL_ACCUMULATION_B_ALERT(32).ENABLE" is set to "1"
|  | 11 | Set "TB.CYCLE_COUNTER_A_ALERT(34).ENABLE" to "1" | "TB.CYCLE_COUNTER_A_ALERT(34).ENABLE" is set to "1"
|  | 12 | Set "TB.CYCLE_COUNTER_B_ALERT(35).ENABLE" to "1" | "TB.CYCLE_COUNTER_B_ALERT(35).ENABLE" is set to "1"
|  | 13 | Set "TB.NEAR_CLOSED_ALERT(39).ENABLE" to "1" | "TB.NEAR_CLOSED_ALERT(39).ENABLE" is set to "1"
|  | 14 | Set "TB.SETPOINT_TIMEOUT_ALERT(41).ENABLE" to "1" | "TB.SETPOINT_TIMEOUT_ALERT(41).ENABLE" is set to "1"
|  | 15 | Set "TB.SUPLAY_PRESSURE_HI_ALERT(52).ENABLE" to "1" | "TB.SUPLAY_PRESSURE_HI_ALERT(52).ENABLE" is set to "1"
|  | 16 | Set "TB.SUPLAY_PRESSURE_LO_ALERT(53).ENABLE" to "1" | "TB.SUPLAY_PRESSURE_LO_ALERT(53).ENABLE" is set to "1"
|  | 17 | Set "TB.SUPLAY_PRESSURE_LOLO_ALERT(54).ENABLE" to "1" | "TB.SUPLAY_PRESSURE_LOLO_ALERT(54).ENABLE" is set to "1"
|  | 18 | Set "TB.TEMPERATURE_HI_ALERT(62).ENABLE" to "1" | "TB.TEMPERATURE_HI_ALERT(62).ENABLE" is set to "1"
|  | 19 | Set "TB.TEMPERATURE_LO_ALERT(63).ENABLE" to "1" | "TB.TEMPERATURE_LO_ALERT(63).ENABLE" is set to "1"
|  | 20 | Set "TB.IP_DRIVE_CURRENT_HI_ALERT(65).ENABLE" to "1" | "TB.IP_DRIVE_CURRENT_HI_ALERT(65).ENABLE" is set to "1"
|  | 21 | Set "TB.IP_DRIVE_CURRENT_LO_ALERT(66).ENABLE" to "1" | "TB.IP_DRIVE_CURRENT_LO_ALERT(66).ENABLE" is set to "1"
|  | 22 | Set value of "TB.TEMPERATURE_HI_ALERT(62).ALERT_POINT" lower than "TB.TEMPERATURE_HI_ALERT(62).TEMPERATURE" | The value of "TB.TEMPERATURE_HI_ALERT(62).ALERT" is "1 (TRUE)"
|  | 23 | Set "TB.SUPLAY_PRESSURE_HI_ALERT(52).ALERT_POINT" lower than "TB.SUPLAY_PRESSURE_HI_ALERT(52).PESSURE" | The value of "TB.SUPLAY_PRESSURE_HI_ALERT(52).ALERT" is "1(TRUE)"
|  | 24 | Use "Smart Assistant" and select "FF Device Content.Write Advanced.Standard type" | "Standard type" is selected
|  | 25 | Read "TB.TRAVEL_ACCUMULATION_A_ALERT(31).ENABLE" | "TB.TRAVEL_ACCUMULATION_A_ALERT(31).ENABLEE" is "0"
|  | 26 | Read "TB.TRAVEL_ACCUMULATION_B_ALERT(32).ENABLE" | "TB.TRAVEL_ACCUMULATION_B_ALERT(32).ENABLEE" is "0"
|  | 27 | Read "TB.CYCLE_COUNTER_A_ALERT(34).ENABLE" | "TB.CYCLE_COUNTER_A_ALERT(34).ENABLE" is "0"
|  | 28 | Read "TB.CYCLE_COUNTER_B_ALERT(35).ENABLE" | "TB.CYCLE_COUNTER_B_ALERT(35).ENABLE" is "0"
|  | 29 | Read "TB.NEAR_CLOSED_ALERT(39).ENABLE" | "TB.NEAR_CLOSED_ALERT(39).ENABLE" is "0"
|  | 30 | Read "TB.SUPLAY_PRESSURE_HI_ALERT(52).ENABLE" | "TB.SUPLAY_PRESSURE_HI_ALERT(52).ENABLE" is "0"
|  | 31 | Read "TB.SUPLAY_PRESSURE_LO_ALERT(53).ENABLE" | "TB.SUPLAY_PRESSURE_LO_ALERT(53).ENABLE" is "0"
|  | 32 | Read "TB.SUPLAY_PRESSURE_LOLO_ALERT(54).ENABLE" | "TB.SUPLAY_PRESSURE_LOLO_ALERT(54).ENABLE" "0"
|  | 33 | Read "TB.TEMPERATURE_HI_ALERT(62).ALERT" | "TB.TEMPERATURE_HI_ALERT(62).ALERT" is "0 (FALSE)"
|  | 34 | Read "TB.SUPLAY_PRESSURE_HI_ALERT(52).ALERT" | "TB.SUPLAY_PRESSURE_HI_ALERT(52).ALERT" is "0(FALSE)"
|  | 35 | Set "TB.DEVIATION_ALERT(26).ENABLE" to "1" | "TB.DEVIATION_ALERT(26).ENABLE" is set to "0"
|  | 36 | Set "TB.POSITION_HI-HI_ALERT(27).ENABLE" to "1" | "TB.POSITION_HI-HI_ALERT(27).ENABLE" is set to "0"
|  | 37 | Set "TB.POSITION_HI_ALERT(28).ENABLE" to "1" | "TB.POSITION_HI_ALERT(28).ENABLE" is set to "0"
|  | 38 | Set "TB.POSITION_LO_ALERT(29).ENABLE" to "1" | "TB.POSITION_LO_ALERT(29).ENABLE" is set to "0"
|  | 39 | Set "TB.POSITION_LOLO_ALERT(30).ENABLE" to "1" | "TB.POSITION_LOLO_ALERT(30).ENABLE" is set to "0"
|  | 40 | Set "TB.TRAVEL_ACCUMULATION_A_ALERT(31).ENABLE" to "1" | "TB.TRAVEL_ACCUMULATION_A_ALERT(31).ENABLEE" is set to "0"
|  | 41 | Set "TB.TRAVEL_ACCUMULATION_B_ALERT(32).ENABLE" to "1" | "TB.TRAVEL_ACCUMULATION_B_ALERT(32).ENABLE" is set to "0"
|  | 42 | Set "TB.CYCLE_COUNTER_A_ALERT(34).ENABLE" to "1" | "TB.CYCLE_COUNTER_A_ALERT(34).ENABLE" is set to "0"
|  | 43 | Set "TB.CYCLE_COUNTER_B_ALERT(35).ENABLE" to "1" | "TB.CYCLE_COUNTER_B_ALERT(35).ENABLE" is set to "0"
|  | 44 | Set "TB.NEAR_CLOSED_ALERT(39).ENABLE" to "1" | "TB.NEAR_CLOSED_ALERT(39).ENABLE" is set to "0"
|  | 45 | Set "TB.SETPOINT_TIMEOUT_ALERT(41).ENABLE" to "1" | "TB.SETPOINT_TIMEOUT_ALERT(41).ENABLE" is set to "0"
|  | 46 | Set "TB.SUPLAY_PRESSURE_HI_ALERT(52).ENABLE" to "1" | "TB.SUPLAY_PRESSURE_HI_ALERT(52).ENABLE" is set to "0"
|  | 47 | Set "TB.SUPLAY_PRESSURE_LO_ALERT(53).ENABLE" to "1" | "TB.SUPLAY_PRESSURE_LO_ALERT(53).ENABLE" is set to "0"
|  | 48 | Set "TB.SUPLAY_PRESSURE_LOLO_ALERT(54).ENABLE" to "1" | "TB.SUPLAY_PRESSURE_LOLO_ALERT(54).ENABLE" is set to "0"
|  | 49 | Set "TB.TEMPERATURE_HI_ALERT(62).ENABLE" to "1" | "TB.TEMPERATURE_HI_ALERT(62).ENABLE" is set to "0"
|  | 50 | Set "TB.TEMPERATURE_LO_ALERT(63).ENABLE" to "1" | "TB.TEMPERATURE_LO_ALERT(63).ENABLE" is set to "0"
|  | 51 | Set "TB.IP_DRIVE_CURRENT_HI_ALERT(65).ENABLE" to "1" | "TB.IP_DRIVE_CURRENT_HI_ALERT(65).ENABLE" is set to "0"
|  | 52 | Set "TB.IP_DRIVE_CURRENT_LO_ALERT(66).ENABLE" to "1" | "TB.IP_DRIVE_CURRENT_LO_ALERT(66).ENABLE" is set to "0"
53