## Sheet1
Title | TestStep | StepAction | StepExpected | Outcome | Comment
Robustness Testing - Setpoint Timeout |  |  |  | Failed
| 1 | Get "RB.0.BLOCK_TAG" | Write down the received block tag. | Passed | 4456440008 03320154
| 2 | Get "RB.SOFTWARE_REV" | Write down the received version of the software, | Passed | 3.1.0.0 CSC90285
| 3 | Set "TB.XD_FSTATE.FSATE_TIME" to "1" and "TB.XD_FSTATE.FSATE_OPT" to "0: Hold Last Value" | The two members of "TB.XD_FSTATE" are set properly | Passed
| 4 | Put t and AO in AUTO. Set AO.SP value to 40% | TB.FINAL_VALUE is 40% | Passed
| 5 | Put TB in AUTO and AO in OOS | TB mode is AUTO and AO mode is OOS | Passed | In case "TB.XD_FSTATE.FSATE_OPT" set to "1 or 2" the valve goes immediately to fully open/close.
| 6 | Set RB.RESTART to 4 | The device is restarted. | Passed
| 7 | Read TB.FINAL_VALUE.SUBSTATUS | The SUBSTATUS is uncertain | Passed
| 8 | Check valve position. | After about a 15 seconds valves goes to de-energized position. | Failed | The valve moves only about 0.5% toward de_energized position. In case "TB.XD_FSTATE.FSATE_OPT" set to "1 or 2" it goes to fully open/close.
| 9 | Set TB.FINAL_VALUE.STATUS to GOOD | The valve returns under control. | Passed
| 10 | Check valve position. | The valve returns under control | Passed
| 11 | Put TB in OOS | TB.FINAL_VALUE.STATUS is BAD | Passed | TB.FINAL_VALUE holds last value.
| 12 | Read TB.FINAL_VALUE.SUBSTATUS | The SUBSTATUS is OutOfService. | Passed
| 13 | Check valve position. | After about a 5 seconds valves goes to de-energized position. | Passed