## Flash failure
TestCaseId | Title | TestStep | StepAction | StepExpected | TestPointId | Configuration | Tester | Outcome | Comment
| Flash failure - RAM glitch |  |  | Emulate RAM glitch in flash test object in FFP. |  | Windows 7
|  | 1 | Find memory address of 'flashtest' in map file. | Memory address of 'flashtest' is known.
|  | 2 | Use SA with HART over FF to introduce RAM fault. | SA is started and connected to the device using HART over FF.
|  | 2.1 | Open 'User Hart Commands' tab. | Tab is located.
|  | 2.2 | Select Hart command - 'Write FFP memory'. | Command is selected - 'Write FFP memory'.
|  | 2.3 | Set 'FFP Memory Selection' to 'FFP RAM'. | FFP Memory Selection' is 'FFP RAM'.
|  | 2.4 | Set 'FFP Memory address' to 'flashtest' address. | FFP Memory address' is 'flashtest' address starting with 0x.
|  | 2.5 | Set 'FFP Memory Block Length' to value 12. | FFP Memory Block Length' is 12.
|  | 2.6 | Set 'FFP Memory Content': | "FFP Memory Content" is set to 24 seros.
|  | 2.6.1 | Enter 24 zeros.
|  | 2.6.2 | Alternatively check 'Disable range checking' and enter only one 0.
|  | 3 | Press 'Send Command'. | Command is executed.
|  | 4 | Verify that the device restarts and continues. | Device is restarted and continues to work normally.

## Flash failure - permanent
TestCaseId | Title | TestStep | StepAction | StepExpected | TestPointId | Configuration | Tester | Outcome | Comment
| Flash failure - permanent |  |  | Emulate RAM glitch in flash test object in FFP. |  | Windows 7
|  | 1 | Find memory address of 'flashtest' in map file. | Memory address of 'flashtest' is known.
|  | 2 | Use SA with HART over FF to introduce RAM fault. | SA is started and connected to the device using HART over FF.
|  | 2.1 | Open 'User Hart Commands' tab. | Tab is located.
|  | 2.2 | Select Hart command - 'Write FFP memory'. | Command is selected - 'Write FFP memory'.
|  | 2.3 | Set 'FFP Memory Selection' to 'FFP RAM'. | FFP Memory Selection' is 'FFP RAM'.
|  | 2.4 | Set 'FFP Memory address' to 'flashtest' address. | FFP Memory address' is 'flashtest' address starting with 0x.
|  | 2.5 | Set 'FFP Memory Block Length' to value 12. | FFP Memory Block Length' is 12.
|  | 2.6 | Set 'FFP Memory Content' to "0 0 0 0 0 0 0 0 0 0 255 255" | "FFP Memory Content" is set to "0 0 0 0 0 0 0 0 0 0 255 255".
|  | 3 | Press 'Send Command'. | Command is executed.
|  | 4 | Verify that the device desconnects from APP. | APP-owned parameters show as NULL.
|  | 5 | Verify that the FF communications are running. | FF communications are running.
|  | 6 | Restart CPU by RB.RESTART | Device is restarted.
|  | 7 | Verify that the device is fully functional after restart. | Device is fully functionall.

## External Watchdog
TestCaseId | Title | TestStep | StepAction | StepExpected | TestPointId | Configuration | Tester | Outcome | Comment
| External Watchdog |  |  |  |  | Windows 7
|  | 1 | Use SA with HART over FF. | SA is started and connected to the device using HART over FF.
|  | 1.1 | Open 'FF Diag' tab. | Tab is located.
|  | 2 | Press 'Clear Device Info' button. | Device info is cleared.
|  | 3 | Make TB mode AUTO | TB mode is AUTO.
|  | 3.1 | How??? NI Dialog?
|  | 4 | Issue RB.RESTART = 30
|  | 4.1 | Open NI Dialog and locate device RB. | Device RB is expanded in NI Dialog and parameters are visible.
|  | 4.2 | Select 'RESTART' parameter and open 'Write Object' dialog. | Parameter 'RESTART' is selected.
|  | 4.3 | Set parameter value of 30. | RESTART value to write is 30.
|  | 4.4 | Press 'Write' button. | Parameter is written and device restart is initiated.
|  | 5 | Verify that device restarts in about 3 sec. | Device reseted and resumed correctly.
|  | 6 | Record TB mode. | TB mode is recorded.
|  | 7 | In SA->'FF Diag' read diagnostic info. | Diagnostic info is read.
|  | 8 | Verify there is an entry with Diag2=-4 | Diag2=-4 is present.

## Internal Watchdog
TestCaseId | Title | TestStep | StepAction | StepExpected | TestPointId | Configuration | Tester | Outcome | Comment
| External Watchdog |  |  |  |  | Windows 7
|  | 1 | Use SA with HART over FF. | SA is started and connected to the device using HART over FF.
|  | 1.1 | Open 'FF Diag' tab. | Tab is located.
|  | 2 | Press 'Clear Device Info' button. | Device info is cleared.
|  | 3 | Make TB mode AUTO | TB mode is AUTO.
|  | 3.1 | How??? NI Dialog?
|  | 4 | Issue RB.RESTART = 30
|  | 4.1 | Open NI Dialog and locate device RB. | Device RB is expanded in NI Dialog and parameters are visible.
|  | 4.2 | Select 'RESTART' parameter and open 'Write Object' dialog. | Parameter 'RESTART' is selected.
|  | 4.3 | Set parameter value of 31. | RESTART value to write is 31.
|  | 4.4 | Press 'Write' button. | Parameter is written and device restart is initiated.
|  | 5 | Verify that device restarts in about 3 sec. | Device reseted and resumed correctly.
|  | 6 | Record TB mode. | TB mode is recorded.
|  | 7 | Verify that APP mode didn't change. | APP did not changed.
|  | 8 | In SA->'FF Diag' read diagnostic info. | Diagnostic info is read.
|  | 9 | Verify there is an entry with Diag2=-8 | Diag2=-8 is present.
|  | 10 | Verify that Diag1 field is non-zero (may take several tries). | Field Diag1 is non-zero.

## Setpoint timeout
TestCaseId | Title | TestStep | StepAction | StepExpected | TestPointId | Configuration | Tester | Outcome | Comment
| Setpoint timeout |  |  |  |  | Windows 7
|  | 1 | Configure TB.XD_FSTATE
|  | 1.1 | How ?
|  | 1.2 | Set 'timeout' to 1. | Timeout is 1.
|  | 1.3 | Set 'option' to 'hold last value'. | "Option" is 'hold last value'.
|  | 2 | Ensure AO FB is not connected () | Device is empty.
|  | 3 | Make TB mode AUTO | TB mode is AUTO.
|  | 4 | Reset device
|  | 4.1 | How ?
|  | 5 | Verify 'FINAL_VALUE' has 'Uncertain' status. | "FINAL_VALUE" status is 'Uncertain'.
|  | 6 | Verify value maintains the position for about 15-16 sec.
|  | 7 | Verify the fault 'SP LOST' is set.
|  | 8 | Verify the valve goes to de-energized position. | Both 'AirToOpen' and 'AirToClose' are ???
|  | 9 | Set 'FINAL_VALUE' status to 'GOOD'.
|  | 9.1 | How ?
|  | 10 | Verify that valve returns under control. | Valve is under control.
|  | 11 | Set 'FINAL_VALUE' status to 'BAD'.
|  | 12 | Verify 'FINAL_VALUE' has 'Uncertain' status.
|  | 13 | Verify valve maintains the position for about 3-4sec.
|  | 14 | Verify the fault 'SP LOST' is set.
|  | 15 | Verify the valve goes to de-energized position. | Both 'AirToOpen' and 'AirToClose' are ???

## Network Parameters
TestCaseId | Title | TestStep | StepAction | StepExpected | TestPointId | Configuration | Tester | Outcome | Comment
| Network Parameters |  |  |  |  | Windows 7
|  | 1 | Ensure network parameters values.
|  | 1.1 | How?
|  | 1.2 | Set 'Max Scheduling Overhead' to 1. | Max Scheduling Overhead' is 1.
|  | 1.x | Set other parameters …..
|  | 2 | Verify device works correctly
|  | 2.1 | How?
|  | 3 | Verify firmware update works correctly.
|  | 3.1 | Use DTM host application and Comm. DTM. | Comm.DTM is connected.
|  | 3.2 | On 'Live List' page select the device.
|  | 3.3 | Use 'Firmware Download' dialog to download a firmware (???).
|  | 3.4 | Verify firmware update process completes successfully.
|  | 3.5 | Verify device is activated.
|  | 4 | Verify device works correctly.
|  | 4.1 | How?

## NV Memory Reinitialization
TestCaseId | Title | TestStep | StepAction | StepExpected | TestPointId | Configuration | Tester | Outcome | Comment
| NV Memory Reinitialization |  |  |  |  | Windows 7
|  | 1 | Use SA and connect to device using HART over FF. | SA is connected to device.
|  | 2 | Open 'FF Diag' tab.
|  | 3 | Clear diagnostic info by pressing 'Clear Device Info' button. | Diagnostic data is cleared.
|  | 4 | Modify some block parameters
|  | 4.1 | How - SA, NI Dialog, or device DTM?
|  | 4.2 | Which parameters?
|  | 5 | Reinitialize NV memory - RB.RESTART = 169
|  | 5.1 | Open NI Dialog and locate device RB. | Device RB is expanded in NI Dialog and parameters are visible.
|  | 5.2 | Select 'RESTART' parameter and open 'Write Object' dialog. | Parameter 'RESTART' is selected.
|  | 5.3 | Set parameter value of 31. | RESTART value to write is 31.
|  | 5.4 | Press 'Write' button. | Parameter is written and device restart is initiated.
|  | 6 | Re-read diagnostic info. | Diagnostic data is read.
|  | 7 | Verify that there is a single entry with Diag2=-4. | Diag2=-4 is present.
|  | 8 | Verify that modified parameters reverted to their defaults. | Parameters reverted.
|  | 9 | Wait at least 30sec. | At least 30 sec passed after previous step.
|  | 10 | Repeat from step 3.

## NV Memory Instrumentation
TestCaseId | Title | TestStep | StepAction | StepExpected | TestPointId | Configuration | Tester | Outcome | Comment
| NV Memory Instrumentation |  |  |  |  | Windows 7
|  | 1 | Find memory address of object 'stat' in map file. | Memory address of 'stat' is known.
|  | 2 | Use SA with HART over FF. | SA is started and connected to the device using HART over FF.
|  | 3 | Open 'User Hart Commands' tab. | Tab is located.
|  | 4 | Read data for APP
|  | 4.1 | Select Hart command - 'read memory?'. | Command is selected.
|  | 4.2 | Set dialog parameter '...' to '???'.
|  | 4.3 | Set dialog parameter '...' to '???'.
|  | 4.4 | Execute command | Command is executed.
|  | 5 | Record the reading.
|  | 6 | Verify that '…_max' values are non-zero.
|  | 7 | Clear those '…_max' values.
|  | 7.1 | Select Hart command - 'write memory?'. | Command is selected.
|  | 7.2 | Set dialog parameter '...' to '???'.
|  | 7.3 | Set dialog parameter '...' to '???'.
|  | 7.4 | Execute command | Command is executed.
|  | 8 | Verify that '…_max' values are non-zero.
|  | 9 | Read data for FP
|  | 9.1 | Select Hart command - 'read memory?'. | Command is selected.
|  | 9.2 | Set dialog parameter '...' to '???'.
|  | 9.3 | Set dialog parameter '...' to '???'.
|  | 9.4 | Execute command | Command is executed.
|  | 10 | Record the reading.
|  | 11 | Verify that '…_max' values are non-zero.
|  | 12 | Clear those '…_max' values.
|  | 12.1 | Select Hart command - 'write memory?'. | Command is selected.
|  | 12.2 | Set dialog parameter '...' to '???'.
|  | 12.3 | Set dialog parameter '...' to '???'.
|  | 12.4 | Execute command | Command is executed.
|  | 13 | Verify that '…_max' values are non-zero.